Modello di Ottimizzazione per una comunità energetica

Obiettivo

The growing emphasis on clean energy transitions and the integration of renewable energy sources has catalysed the emergence of energy communities. These communities foster collective action to enhance energy efficiency, lower costs, and support local job creation. However, their integration into the energy system introduces challenges, particularly regarding the effective management of energy surpluses and deficits. Daily and seasonal energy storage systems, such as lithium and hydrogen technologies, play a pivotal role in addressing these imbalances.

Developing cost-efficient strategies for managing storage systems requires advanced modelling approaches, particularly those incorporating dynamic decision-making variables, diverse energy sources, and real-time energy demand patterns.

We now describe the problem which consists of minimizing the power exchanged with an external electricity supply network (grid). This can be interpreted as minimizing the total energy transferred to or drawn from the grid, reducing the costs associated with purchasing energy from the grid, or maximizing self-consumption to decrease dependency on the external network.

The solutions that we propose consists in:

- Offline best solution. Given as input the energy productions and the energy consumptions (expressed in Kw/h) of each hour of a particular day, we want to calculate the best quantity of energy to be taken from the battery such that, at the end of the day, the battery is almost completely discharged (or it is almost near the minimum quantity of energy that is possible). Note that the quantity of production and consumption can be the results of a prediction made from the ML model

- Realtime best solution. Given the quantity of productions and the energy consumptions of the previous time t – 1 (eg. the last 15 minutes of the last 1 hour), calculate the best quantity of energy to be taken at time t (now) knowing the predicted production and consumption.

Descrizione modello di ottimizzazione

Funzione obiettivo: come funzione obiettivo vi è la minimizzazione di una funzione della potenza scambiata con la rete. Ciò si può tradurre in una minimizzazione dell’energia complessiva scambiata con la rete, una minimizzazione dei costi legati all’acquisto dell’energia dalla rete, o anche massimizzazione dell’autoconsumo.

OF:t=1 d=1 D T f(Pgtd)                                    (1)

Vincoli

Pgtd=PLtd-PPVtd-PStd 		(2)

ESt+1d=EStd+PStd*t 		(3)

ESmin≤EStd≤ESmax 		(4)

PSmin≤ PStd≤PSmax 		(5)

ESt=1d=1=ESInit			(6)

| Nomenclatura |  | Dettagli |
| --- | --- | --- |
| Pgtd | Grid Transferred Power; (time t, day d) | Quantity of Power exchanged with the grid. If it is positive, it refers to the power taken from the grid. If it is negative, it refers to the power fed to the grid. |
| PLtd | Load Power; (time t, day d) | Consumption at day d and time t |
| PPVtd | Production Power; (time t, day d) | Production at day d and time t |
| PStd | Storage Transferred Power; (time t, day d) | Quantity of power charged/discharged from the battery. If it is positive, it refers to the quantity of power to charge the battery. If it is negative it refers to the quantity of power taken from the battery (discharge) |
| EStd | Storage Energy Level; (time t, day d) | Storage level of the battery |
| ESmin, ESmax | Minimum and maximum Storage Energy Level | Minimum and maximum storage energy level of the battery. If refers that the storage energy lever must be never lower than ESmin and never greater than ESmax |
| PSmin, PSmax | Minimum and maximum Storage Power | Minimum and maximum storage energy level of the battery. If refers that the storage energy lever must be never lower than ESmin and never greater than ESmax |
| ESInit | Initial Energy stored |  |

I vincoli più importanti del modello sono di seguito descritti.

Il vincolo (2) è un vincolo di uguaglianza funzionale, che considera l’equilibrio delle potenze (potenza di rete, di produzione da PV, del carico e dello storage).

Il vincolo (3) e (4) sono relativi allo storage ed in particolare il (3) determina l’energia immagazzinata nello storage, aggiungendo/sottraendo quella assorbita/erogata. Mentre il vincolo (4) limita l’energia immagazzinata nello storage tra un massimo e un minimo.

Il vincolo (5) è sempre relativo allo storage e limita la potenza che può essere scambiata dallo stesso, generalmente dovuto a motivi costruttivi).

Il modello è molto base ed è relativo al singolo utente o comunque all’aggregazione di utenti. Andranno poi considerati i singoli utenti che costituiscono la comunità, con vincoli analoghi ma che evolvono anche con un indice relativo al singolo utente.

Input

- Production and Consumption for each day d and time t PPVtd and PLtd

- Initial Energy stored at the beginning of the day ESInit

- Minimum and maximum Storage Energy Level ESmin and ESmax

- Minimum and maximum Storage Power Level for a day d and time t PSmin and PSmax

Output

- Grid Transferred Power; (time t, day d) Pgtd

- Storage Transferred Power; (time t, day d) PStd